## bus
Bus | Type | Demand | Demand | Shunt Conductance | Shunt Susceptance | Area | Voltage | Voltage | Base Voltage | Loss Zone | Maximum Voltage | Minimum Voltage
Integer | PQ(1), PV(2), Slack(3) | Active Power [MW] | Reactive Power [MVAr] | Active Power [MW] | Reactive Power [MVAr] | Integer | Magnitude [p.u.] | Angle [deg] | Magnitude [kV] | Integer | Magnitude [p.u.] | Magnitude [p.u.]
1 | 3 | 0 | 0 | 0 | 0 | 1 | 1.06 | 0 | 0 | 1 | 1.06 | 0.94
2 | 2 | 21.7 | 12.7 | 0 | 0 | 1 | 1.045 | -4.98 | 0 | 1 | 1.06 | 0.94
3 | 2 | 94.2 | 19 | 0 | 0 | 1 | 1.01 | -12.72 | 0 | 1 | 1.06 | 0.94
4 | 1 | 47.8 | -3.9 | 0 | 0 | 1 | 1.019 | -10.33 | 0 | 1 | 1.06 | 0.94
5 | 1 | 7.6 | 1.6 | 0 | 0 | 1 | 1.02 | -8.78 | 0 | 1 | 1.06 | 0.94
6 | 2 | 11.2 | 7.5 | 0 | 0 | 1 | 1.07 | -14.22 | 0 | 1 | 1.06 | 0.94
7 | 1 | 0 | 0 | 0 | 0 | 1 | 1.062 | -13.37 | 0 | 1 | 1.06 | 0.94
8 | 2 | 0 | 0 | 0 | 0 | 1 | 1.09 | -13.36 | 0 | 1 | 1.06 | 0.94
9 | 1 | 29.5 | 16.6 | 0 | 19 | 1 | 1.056 | -14.94 | 0 | 1 | 1.06 | 0.94
10 | 1 | 9 | 5.8 | 0 | 0 | 1 | 1.051 | -15.1 | 0 | 1 | 1.06 | 0.94
11 | 1 | 3.5 | 1.8 | 0 | 0 | 1 | 1.057 | -14.79 | 0 | 1 | 1.06 | 0.94
12 | 1 | 6.1 | 1.6 | 0 | 0 | 1 | 1.055 | -15.07 | 0 | 1 | 1.06 | 0.94
13 | 1 | 13.5 | 5.8 | 0 | 0 | 1 | 1.05 | -15.16 | 0 | 1 | 1.06 | 0.94
14 | 1 | 14.9 | 5 | 0 | 0 | 1 | 1.036 | -16.04 | 0 | 1 | 1.06 | 0.94

## branch
Branch | From Bus | To Bus | Series Parameter | Series Parameter | Charging Parameter | Long Term Rate | Short Term Rate | Emergency Rate | Transformer | Transformer | Status | Minimum Voltage Difference | Maximum Voltage Difference
Integer | Integer | Integer | Resistance [p.u.] | Reactance [p.u.] | Susceptance [p.u.] | Power [MVA] | Power [MVA] | Power [MVA] | Turns Ratio | Shift Angle [deg] | Integer | Angle [deg] | Angle [deg]
1 | 1 | 2 | 0.01938 | 0.05917 | 0.0528 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
2 | 1 | 5 | 0.05403 | 0.22304 | 0.0492 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
3 | 2 | 3 | 0.04699 | 0.19797 | 0.0438 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
4 | 2 | 4 | 0.05811 | 0.17632 | 0.034 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
5 | 2 | 5 | 0.05695 | 0.17388 | 0.0346 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
6 | 3 | 4 | 0.06701 | 0.17103 | 0.0128 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
7 | 4 | 5 | 0.01335 | 0.04211 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
8 | 4 | 7 | 0 | 0.20912 | 0 | 0 | 0 | 0 | 0.978 | 0 | 1 | -360 | 360
9 | 4 | 9 | 0 | 0.55618 | 0 | 0 | 0 | 0 | 0.969 | 0 | 1 | -360 | 360
10 | 5 | 6 | 0 | 0.25202 | 0 | 0 | 0 | 0 | 0.932 | 0 | 1 | -360 | 360
11 | 6 | 11 | 0.09498 | 0.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
12 | 6 | 12 | 0.12291 | 0.25581 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
13 | 6 | 13 | 0.06615 | 0.13027 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
14 | 7 | 8 | 0 | 0.17615 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
15 | 7 | 9 | 0 | 0.11001 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
16 | 9 | 10 | 0.03181 | 0.0845 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
17 | 9 | 14 | 0.12711 | 0.27038 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
18 | 10 | 11 | 0.08205 | 0.19207 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
19 | 12 | 13 | 0.22092 | 0.19988 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360
20 | 13 | 14 | 0.17093 | 0.34802 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -360 | 360

## generator
Bus | Generation | Generation | Maximum Generation | Minimum Generation | Voltage | Base | Status | Maximum Generation | Minimum Generation | Lower of PQ Curve | Upper of PQ Curve | Minimum at PC1 | Maximum at PC1 | Minimum at PC2 | Maximum at PC2 | Ramp Rate ACG | Ramp Rate 10 | Ramp Rate 30 | Ramp Rate Q | Area Factor
Integer | Active Power [MW] | Reactive Power [MVAr] | Reactive Power [MVAr] | Reactive Power [MVAr] | Magnitude [p.u.] | Power [MVA] | Integer | Active Power [MW] | Active Power [MW] | Active Power [MW] | Active Power [MW] | Reactive Power [MVAr] | Reactive Power [MVAr] | Reactive Power [MVAr] | Reactive Power [MVAr] | Active Power per Minut [MW/min] | Active Power [MW] | Active Power [MW] | Reactive Power per Minut [MVAr/min] | Integer
1 | 232.4 | -16.9 | 10 | 0 | 1.06 | 100 | 1 | 332.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 40 | 42.4 | 50 | -40 | 1.045 | 100 | 1 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 23.4 | 40 | 0 | 1.01 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 12.2 | 24 | -6 | 1.07 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 17.4 | 24 | -6 | 1.09 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## generatorcost
Cost Model | Cost | Cost | Cost Model | Cost Model | Cost Model | Cost Model
Piecewise(1), Polynomial(2) | Startup [currency] | Shutdown [currency] | Number of Data Points | Coefficient c2 | Coefficient c1 | Coefficient c0
2 | 0 | 0 | 3 | 0.043029 | 20 | 0
2 | 0 | 0 | 3 | 0.25 | 20 | 0
2 | 0 | 0 | 3 | 0.01 | 40 | 0
2 | 0 | 0 | 3 | 0.01 | 40 | 0
2 | 0 | 0 | 3 | 0.01 | 40 | 0

## basePower
Base Power
Power [MVA]
100

## info
Reference | https://labs.ece.uw.edu/pstca/pf14/pg_tca14bus.htm
Data | case14
Grid | transmission
Bus | 14
PV bus | 5
PQ bus | 8
Shunt element | 1
Generator | 5 | 5 in-service
Branch | 20 | 20 in-service
Transformer | 3 | 3 in-service